Current Transducer CH-C-0017-0401

* CH-C-0017-0401 is a Hall-Effect current transducer .

* It can be used for the detection of DC, AC, pulse.

| Electrical data |
| --- |
| IPN | Primary nominal r.m.s current | 17 | A |
| IP | Primary current, measuring range | 0…+32 | A |
| RM | Measuring resistance @ TA =100(C |
|  |  | RM min | RM max |  |
|  | with ( 12 V | @(50Amax | 0 | 219.84 | ( |
|  |  | @(80 Amax | 0 | 147.84 | ( |
|  | with ( 15 V | @(50 Amax | 0 | 279.84 | ( |
|  |  | @(80 Amax | 0 | 167.34 | ( |
| ISN | Secondary nominal r.m.s current | 34 | mA |
| KN | Conversion ratio | 1:500 |  |
| VC | Supply voltage (( 5%) | +12…15 | V |
| IC | Idle current consumption | 15(@+15V) | mA |
| Vd | AC isolation test, 50 Hz, 1min | 3 | kV |

| Accuracy – Dynamic performance data |
| --- |
| X | Accuracy @ IPN , TA = 25(C @ + 15V (( 5%) f=1kHz | ( 0.40 | % |
| (L | Linearity | < 0.15 | % |
| IO | Offset current @ IP = 0, TA = 25(C @(100 Amax 0 0 | ( 0.20 | mA |
| IOM | Residual current @ IP = 0, after an overload of 3 ( IPN 0 | ( 0.30 | mA |
| IOT | Thermal drift of IO (-10℃…+100℃) @(100 Amax | ( 0.40 | mA |
| tr | Response time @ 90% of IPN | < 3 | (s |
| di/dt | di/dt accurately followed | >100 | A/(s |
| f | Frequency bandwidth (-1 dB) | DC…200 | kHz |

| General data |
| --- |
| TA | Ambient operating temperature | -10..+100 | (C |
| M | Mass | 20 | g |

.

Mechanical Characteristic:  General tolerance  ±0.1mm

Remarks

- IS is positive when IP flows in the direction of the arrow.

- Temperature of the primary conductor should not exceed 100 (C.

# Text boxes

Advantages

- Excellent accuracy

- Very good linearity

- Low temperature drift

Special features

- Printed circuit board mounting.

Features

- Closed loop (compensated) current transducer using the Hall-Effect

IPN = 17 A

Applications

- AC variable speed drives and servo motor drives

- Static converters for DC motor drives

- Battery supplied applications

- Uninterruptible Power Supplies (UPS)

- Switched Mode Power Supplies(SMPS)

- Power supplies for welding applications.

* * * * * * * * * * * * * * * * * *

## SECONDARY TERMINALS

TERMINAL +：SUPPLY VOLTAGE +12…15V

TERMINAL M：MEASURE