CH-C-0025-0008(b)                     * CH-C-0500-0008(b) is a Hall-Effect current transducer.

IPN = 250mA

Current Transducer                              * It can be used for the detection of DC, AC, pulse.

Applications

- AC variable speed drives and servo motor drives

- Static converters for DC motor drives

- Battery supplied applications

- Uninterruptible Power Supplies(UPS)

- Switched Mode Power Supplies (SMPS)

- Power supplies for welding applications.

Advantages

- Excellent accuracy

- Very good linearity

- Low temperature drift

Special features

- Connection to secondary circuit

on 2510-3Y connector.

Features

- Closed loop (compensated) current transducer using the Hall-Effect

| # Electrical data |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| IPN | Primary nominal r.m.s current |  |  |  |  |  |  | 250 | mA |  |
| IP | Primary current, measuring range |  |  |  |  |  |  | 0… 300 | mA |  |
| ISN | Secondary nominal r.m.s current |  |  |  |  |  |  | 25 | mA |  |
| KN | Conversion ratio |  |  |  |  |  |  | 10:1000 |  |  |
| VC | Supply voltage ( 5%) |  |  |  |  |  |  |  15 | V |  |
| IC | Idle Current consumption |  |  |  |  |  |  | 15(@ 15) | mA |  |
| Vd | AC isolation test, 50 Hz, 1min |  |  |  |  |  |  | 3 | kV |  |
|  |  | IP |  |  |  |  |  | Ua |  |  |
|  | with  15V | @250Amax |  |  |  |  |  | 4.167 |  | V |
|  |  | @300 Amax |  |  |  |  |  | 5.000 |  | V |

| # Accuracy – Dynamic performance data |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| X | Accuracy @ IPN , TA = 25C | @  15V ( 5%) |  |  |  |  |   0.4 |  |  |  | % |
| L | Linearity |  |  |  |  |  | < 0.15 |  |  |  | % |
| IO | Offset current @ IP = 0, TA = 25C @100 Amax 0 |  |  |  |  | max |  6 |  |  |  | mA |
| IOM | Residual current @ IP = 0, after an overload of 3  IPN 0 |  |  |  |  |  |  0.20 | mA |  |  |  |
| IOT | Thermal drift of IO @100 Amax | (0℃…+100℃) |  |  |  |  |  0.35 |  |  |  | mA |
| tr | Response time @ 90% of IPN |  |  |  |  |  | <3 |  |  |  | s |
| di/dtt | di/dt accurately followed |  |  |  |  |  | >100 |  |  | A/us |  |
| f | Frequency bandwidth (-1 dB) |  |  |  |  |  | DC…100 |  |  | kHz |  |

| # General data |  |  |  |  |
| --- | --- | --- | --- | --- |
| TA | Ambient operating temperature |  | -10..+100 | C |
| M | Mass |  | 222 | g |

## SECONDARY TERMINALS

TERMINAL  Ua: OUTPUT MEASURE

TERMINAL  - :SUPPLY VOLTAGE –15V

TERMINAL  + :SUPPLY VOLTAGE +15V

TERMINAL  0: 0V

TERMINAL  +HT: IN

TERMINAL  -HT: OUT

Remarks

·IS is positive when Ip flows from terminals +HT to –HT.

·This is a standard model .For different versions (supply voltages,turns ratios,unidirectional measurements….), please contact us.