IPN =50 A

Current Transducer CH-C-0050-0202

* CH-C-0050-0202 is a Hall-Effect current transducer.

* It can be used for the detection of DC, AC, pulse.

| # Electrical data |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| IPN | Primary nominal r.m.s current |  |  |  |  |  |  | 50 |  |  |  | A |
| IP | Primary current, measuring range |  |  |  |  |  |  | 0… 100 |  |  |  | A |
| RM | Measuring resistance @ |  |  | TA = 100C |  |  |  |  |  |  |  |  |
|  |  |  |  |  | RM min |  |  |  | RM max |  |  |  |
|  | with  12 V | @50Amax |  |  | 0 |  |  |  | 320 |  |  |  |
|  |  | @100Amax |  |  | 0 |  |  |  | 106 |  |  |  |
|  | with  15 V | @50Amax |  |  | 0 |  |  |  | 336 |  |  |  |
|  |  | @100Amax |  |  | 0 |  |  |  | 165 |  |  |  |
| ISN | Secondary nominal r.m.s current |  |  |  |  |  |  | 25 |  |  |  | mA |
| KN | Conversion ratio |  |  |  |  |  |  | 1:2000 |  |  |  |  |
| VC | Supply voltage ( 5%) |  |  |  |  |  |  |  12…15 |  |  |  | V |
| IC | Idle current consumption |  |  |  |  |  |  | 15(@15V) |  |  |  | mA |
| Vd | AC isolation test, 50 Hz, 1min |  |  |  |  |  |  | 3 |  |  |  | kV |

| Accuracy – Dynamic performance data |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| X | Accuracy @ IPN , TA = 25C |  | @  15V ( 5%) |  |  |  |  0.40 |  |  | % |
| L | Linearity |  |  |  |  |  | < 0.15 |  |  | % |
| IO | Offset current @ IP = 0, TA = 25C @100 Amax 0 0 |  |  |  |  |  0.20 |  |  |  | mA |
| IOM | Residual current @ IP = 0, after an overload of 3  IPN 0 |  |  |  |  |  0.30 |  |  |  | mA |
| IOT | Thermal drift of IO @100 Amax | (-10℃…+100℃) |  |  |  |  0.40 |  |  |  | mA |
| tr | Response time @ 90% of IPN |  |  |  |  |  | <3 |  |  | s |
| di/dtt | di/dt accurately followed |  |  |  |  |  | >100 |  | A/us |  |
| f | Frequency bandwidth (-1 dB) |  |  |  |  |  | DC…200 |  |  | kHz |

| # General data |  |  |  |  |
| --- | --- | --- | --- | --- |
| TA | Ambient operating temperature |  | -10..+100 | C |
| M | Mass |  | 25 | g |

Features

- Closed loop (compensated) current transducer using the Hall-Effect

Advantages

- Excellent accuracy

- Very good linearity

- Low temperature drift

Applications

- AC variable speed drives and servo motor drives

- Static converters for DC motor drives

- Battery supplied applications

- Uninterruptible Power Supplies (UPS)

- Switched Mode Power Supplies(SMPS)

- Power supplies for welding applications.

Special features

- Printed circuit board mounting.

Remarks

- IS is positive when IP flows in the direction of the arrow.

- Temperature of the primary conductor should not exceed100 C.