IPN = 125A

Current Transducer CH-C-0125-0001

* CH-C-0125-0001 is a Hall-Effect current transducer.

* It can be used for the detection of DC, AC, pulse.

| ## Electrical data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| IPN | Primary nominal r.m.s current |  |  | 125 | A |
| IP | Primary current, measuring range |  |  | 0… 200 | A |
| RM | Measuring resistance @ TA = 100C |  |  |  |  |
|  |  |  | RM min | RM max |  |
|  | with  12 V | @ 125 Amax | 0 | 90 |  |
|  |  | @200 Amax | 0 | 54 |  |
|  | with  15 V | @ 125 Amax | 0 | 113 |  |
|  |  | @200 Amax | 0 | 69 |  |
| ISN | Secondary nominal r.m.s current |  |  | 125 | mA |
| KN | Conversion ratio |  |  | 1 : 1000 |  |
| VC | Supply voltage ( 5%) |  |  |  12…15 | V |
| IC | Idle current consumption |  |  | 19(@15V)+IS | mA |
| Vd | AC isolation test, 50 Hz, 1min |  |  | 5 | kV |

| Accuracy – Dynamic performance data |  |  |  |
| --- | --- | --- | --- |
| X | Accuracy @ IPN , TA = 25C @  15V ( 5%) f=1kHz |   0.41 | % |
| L | Linearity | < 0.15 | % |
| IO | Offset current @ IP = 0, TA = 25C @100 Amax 0 0 |  0.20 | mA |
| IOM | Residual current @ IP = 0, after an overload of 3  IPN 0 |  0.20 | mA |
| IOT | Thermal drift of IO (-10C…+100C) @100 Amax |  0.95 | mA |
| tr | Response time @ 90% of IPN | < 1 | s |
| di/dt | di/dt accurately followed | >100 | A/s |
| f | Frequency bandwidth (-1 dB) | DC…100 | kHz |

| ## General data |  |  |  |
| --- | --- | --- | --- |
| TA | Ambient operating temperature | -40..+85 | C |
| M | Mass | 28 | g |

Features

- Closed loop (compensated) current transducer using the Hall-Effect

125

Applications

- AC variable speed drives and servo motor drives

- Static converters for DC motor drives

- Battery supplied applications

- Uninterruptible Power Supplies (UPS)

- Switched Mode Power Supplies(SMPS)

- Power supplies for welding applications.

Advantages

- Excellent accuracy

- Very good linearity

- Low temperature drift

Special features

- Printed circuit board mounting.

* * * * * * * * * * * * * * * * * *

## SECONDARY TERMINALS

TERMINAL +：SUPPLY VOLTAGE +12…15V

TERMINAL M：MEASURE

TERMINAL -：SUPPLY VOLTAGE  -12…15V

PRIMARY TERMINALS 1-3：IN

PRIMARY TERMINALS 4-6：OUT

125

Mechanical Characteristic:  General tolerance  ±0.1mm

### Remarks

.Is is positive when Ip flows from terminals 1,2,3 to terminals 4,5,6

.This is a standard model .For different versions (supply voltages,turns ratios,unidirectional measurements….), please contact us.