IPN = 200 A

Current Transducer CH-C-0200-1608

* CH-C-0200-1608 is a Hall-Effect current transducer.

* It can be used for the detection of DC, AC, pulse.

| # Electrical data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| IPN | Primary nominal r.m.s current |  |  | 200 | A |
| IP | Primary current, measuring range |  |  | 0… 420 | A |
| RM | Measuring resistance @ TA = 100C |  |  |  |  |
|  |  |  | RM min | RM max |  |
|  | with  12 V | @200 Amax | 0 | 74 |  |
|  |  | @300 Amax | 0 | 36 |  |
|  | with  15 V | @200 Amax | 0 | 100 |  |
|  |  | @420 Amax | 0 | 30 |  |
| ISN | Secondary nominal r.m.s current |  |  | 100 | mA |
| KN | Conversion ratio |  |  | 1:2000 |  |
| VC | Supply voltage ( 5%) |  |  |  12…15 | V |
| IC | Idle current consumption |  |  | 36(@15V) | mA |
| Vd | AC isolation test, 50 Hz, 1min |  |  | 3 | kV |

| Accuracy – Dynamic performance data |  |  |  |
| --- | --- | --- | --- |
| X | Accuracy @ IPN , TA = 25C @  15V ( 5%) f=1kHz |  0.40 | % |
| L | Linearity | < 0.15 | % |
| IO | Offset current @ IP = 0, TA = 25C @100 Amax 0 0 |  0.20 | mA |
| IOM | Residual current @ IP = 0, after an overload of 3  IPN 0 |  0.30 | mA |
| IOT | Thermal drift of IO (-10℃…+100℃) @100 Amax |  0.40 | mA |
| tr | Response time @ 90% of IPN | <3 | s |
| di/dt | di/dt accurately followed | >100 | A/s |
| f | Frequency bandwidth (-1 dB) | DC…100 | kHz |

| # General data |  |  |  |
| --- | --- | --- | --- |
| TA | Ambient operating temperature | -10..+100 | C |
| M | Mass | 50 | g |

Advantages

- Excellent accuracy

- Very good linearity

- Low temperature drift

Features

- Closed loop (compensated) current transducer using the Hall-Effect

Applications

- AC variable speed drives and servo motor drives

- Static converters for DC motor drives

- Battery supplied applications

- Uninterruptible Power Supplies (UPS)

- Switched Mode Power Supplies(SMPS)

- Power supplies for welding applications.

Special features

- Connection to secondary circuit

on 2510-3Y connector.

* * * * * * * * * * * * * * * * * *

SECONDARY TERMINALS

TERMINAL +：SUPPLY VOLTAGE +12…15V

TERMINAL M：MEASURE

TERMINAL -：SUPPLY VOLTAGE  -12…15V

Mechanical Characteristic:  General tolerance  ±0.1mm

Remarks

- IS is positive when IP flows in the direction of the arrow.

- Temperature of the primary conductor should not exceed 100C.