CH-C-0500-1602                                * CH-C-0500-1602 is a Hall-Effect current transducer.

Current Transducer                              * It can be used for the detection of DC, AC, pulse.

| Electrical data |
| --- |
| IPN | Primary nominal r.m.s current | 500 | A |
| IP | Primary current, measuring range | 0…( 800 | A |
| ISN | Secondary nominal r.m.s current | 250 | mA |
| KN | Conversion ratio | 1:2000 |  |
| VC | Supply voltage (( 5%) | (12…15 | V |
| IC | Idle Current consumption | 36(@(15) | mA |
| Vd | AC isolation test, 50 Hz, 1min | 3 | kV |
| RM | Measuring resistance @ TA = 100(C |  |  |
|  |  | RM min | RM max |  |
|  | with ( 12V | @(500Amax | 0 24 | ( |
|  |  | @(800 Amax | 0 8 | ( |
|  | with ( 15V | @(500 Amax | 0 36 | ( |
|  |  | @(800 Amax | 0 16 | ( |
| Accuracy – Dynamic performance data |
| X | Accuracy @ IPN , TA = 25(C @ ( 15V (( 5%) | ( 0.40 | % |
| (L | Linearity | < 0.15 | % |
| IO | Offset current @ IP = 0, TA = 25(C @(100 Amax 0 0 | ( 0.20 | mA |
| IOM | Residual current @ IP = 0, after an overload of 3 ( IPN 0 | ( 0.30 | mA |
| IOT | Thermal drift of IO (-10℃…+100℃) @(100 Amax | ( 0.50 | mA |
| tr | Response time @ 90% of IPN | <3 | (s |
| di/dt | di/dt accurately followed | >100 | A/(s |
| f | Frequency bandwidth (-1 dB) | DC…100 | kHz |

| General data |
| --- |
| TA | Ambient operating temperature | -10..+100 | (C |
| m | Mass | 250 | g |

Remarks

- IS is positive when IP flows in the direction of the arrow.

- Temperature of the primary conductor should not exceed 100 (C.

# Text boxes

IPN=500 A

Applications

- AC variable speed drives and servo motor drives

- Static converters for DC motor drives

- Battery supplied applications

- Uninterruptible Power Supplies(UPS)

- Switched Mode Power Supplies (SMPS)

- Power supplies for welding applications.

Features

- Closed loop (compensated) current transducer using the Hall-Effect

Advantages

- Excellent accuracy

- Very good linearity

- Low temperature drift

Special features

- Connection to secondary circuit

on 2510-4A/W connector.

* * * * * * * * * * * * * * * * *

SECONDARY TERMINALS

TERMINAL NC：

TERMINAL +：SUPPLY VOLTAGE +12…15V

TERMINAL M：MEASURE

TERMINAL -：SUPPLY VOLTAGE  -12…15V