CH-C-0500-1606                               * CH-C-0500-1606 is a Hall-Effect current transducer.

IPN=500 A

Current Transducer                              * It can be used for the detection of DC, AC, pulse.

Applications

- AC variable speed drives and servo motor drives

- Static converters for DC motor drives

- Battery supplied applications

- Uninterruptible Power Supplies(UPS)

- Switched Mode Power Supplies (SMPS)

- Power supplies for welding applications.

Advantages

- Excellent accuracy

- Very good linearity

- Low temperature drift

Special features

- Connection to secondary circuit

on 2510-3Y connector.

Features

- Closed loop (compensated) current transducer using the Hall-Effect

| # Electrical data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| IPN | Primary nominal r.m.s current |  | 500 | A |  |
| IP | Primary current, measuring range |  | 0… 800 | A |  |
| ISN | Secondary nominal r.m.s current |  | 125 | mA |  |
| KN | Conversion ratio |  | 1:4000 |  |  |
| VC | Supply voltage ( 5%) |  | ±12… 24 | V |  |
| IC | Idle Current consumption |  | 12 | mA |  |
| Vd | AC isolation test, 50 Hz, 1min |  | 3 | kV |  |
| RM | Measuring resistance @ TA = 100C |  |  |  |  |
|  |  |  | R M min | RM max |  |
|  | with  12V | @500Amax | 0 33 |  |  |
|  |  | @800 Amax | 0 2 |  |  |
|  | with  24V | @500 Amax | 14 120 |  |  |
|  |  | @800 Amax | 7 56 |  |  |
| # Accuracy – Dynamic performance data |  |  |  |  |  |
| X | Accuracy @ IPN , TA = 25C @  24V ( 5%) |  |  0.40 |  | % |
| L | Linearity |  | < 0.15 |  | % |
| IO | Offset current @ IP = 0, TA = 25C @100 Amax 0 0 |  |  0.40 |  | mA |
| IOT | Thermal drift of IO (-10℃…+100℃) @100 Amax |  |  0.40 |  | mA |
| tr | Response time @ 90% of IPN |  | <3 |  | s |
| di/dt | di/dt accurately followed |  | >100 |  | A/s |
| f | Frequency bandwidth (-1 dB) |  | DC…100 |  | kHz |

| # General data |  |  |  |
| --- | --- | --- | --- |
| TA | Ambient operating temperature | -10..+100 | C |
| m | Mass | 256.9 | g |

* * * * * * * * * * * * * * * * * *

SECONDARY TERMINALS

TERMINAL +：SUPPLY VOLTAGE +12…24V

TERMINAL M：MEASURE

TERMINAL -：SUPPLY VOLTAGE  -12…24V

Remarks

- IS is positive when IP flows in the direction of the arrow.

- Temperature of the primary conductor should not exceed 100 C.