Current Transducer CH-C-0800-1401                   IPN = 800At

* CH-C-0800-1401 is a Hall-Effect current transducer.

* It can be used for the detection of DC, AC, pulse.

| Electrical data |
| --- |
| IPN | Primary nominal r.m.s current | 800 | At |
| IP | Primary current, measuring range | 0…( 1200① | At |
| Vout | Analog output voltage @ Ip Ip=0 | 2.5±(1.25·IP / IPN) | V |
|  | Ip=0 | 2.5 ±0.025② | V |
| Ns | Number of secondary turns ((0.1%) | 2000 |  |
| RL | Load resistance | ≥200 | k( |
| VC | Supply voltage (( 5%) | 5 | V |
| IC | Current consumption @ VC =5V | 22 | mA |
| ROUT | Output impedance | ≥2 | k( |

| Accuracy – Dynamic performance data |
| --- |
| X | Accuracy @ IPN , TA = 25(C @5V (( 5%) f=1kHz | (1 | % |
|  | Accuracy with RIM @ IPN,TA=25(C | ( 0.60 | % |
| εL | Linearity error | < ( 0.50 | % |
| TCVOUT | Thermal drift of VOUT / VREF @ IP=0 -10(C..+100(C | < ( 0.30 | mV/K |
| TCVG | Thermal drift of the gain -10(C..+100(C | < ( 0.50 | mV/K |
| VOM | Residual voltage @ Ip=0,after an overload of 3 x IPN | < ( 0.50 | %ofIPN |
| tr | Response time @ 90% of IPN | <7 | us |
| di/dt | di/dt accurately followed | >100 | A/(s |
| f | Frequency bandwidth(-1dB) | DC..20 | kHz |

| General data |
| --- |
| TA | Ambient operating temperature | -10..+100 | (C |
| M | Mass | 110 | g |

Mechanical Characteristic:  General tolerance  ±0.1mm

Notes:   ①Only in refout mode or  with external REF less than 2.525V and greater than 2.475V.

②Absolute value @ TA = 25(C  ,2.475V< VREF <2.525V

③ The primary winding is with 3 wires parallel.

# Text boxes

Advantages

- Excellent accuracy

- Very good linearity

- Low temperature drift

Special features

- Printed circuit board mounting.

- Unipolar voltage supply.

Features

- Closed loop (compensated) current transducer using the Hall-Effect

Applications

- AC variable speed drives and servo motor drives

- Static converters for DC motor drives

- Battery supplied applications

- Uninterruptible Power Supplies (UPS)

- Switched Mode Power Supplies(SMPS)

- Power supplies for welding applications.