CH-O-0050-0002                     * CH-O-0050-0002 is a Hall-Effect current transducer.

IPN = 50A

Current Transducer                              * It can be used for the detection of DC, AC, pulse.

NO PHOTO

Advantages

- Easy mounting.

- Small size and space savings.

- Only one design for wide current ratings range.

- High immunity against external interference.

- Current overload capability.

- Adjustable output gain.

- Adjustable offset to zero.

Features

- Hall effect measuring principle.

- Galvanic isolation between primary and secondary circuit.

- Low power consumption.

Applications

- AC motor speed control.

- Static converters for DC motor drives.

- Battery supplied applications.

- Uninterruptible Power Supplies (UPS).

- Power supplies for welding, cable TV and telecommunication applications.

| # Electrical data |  |  |  |
| --- | --- | --- | --- |
| IPN | Primary nominal r.m.s current | 50 | A |
| IP | Primary current, measuring range |  150 | A |
| Vout | Analog output voltage @ Ip Ip=0 | VREF±(0.625·IP / IPN) | V |
|  | Ip=0 | VREF±0.0125 | V |
| VREF | Internal Reference① Output voltage | 2.5±0.025 | V |
|  | VREF Output impedance | Typ. 200 |  |
|  | VREF Load impedance | ≥200 |  |
| RL | Output load resistance | ≥2 | k |
| Rout | Output impedance | <10 |  |
| CL | Max.output capacitive load | <1 | uF |
| VC | Supply voltage (± 5%) | 5 | V |
| IC | Idle current consumption @ VC =5V IP=0 | 22 | mA |

| # Accuracy – Dynamic performance data |  |  |  |  |
| --- | --- | --- | --- | --- |
| X | Accuracy @ IPN , TA = 25℃ | 5V (± 5%) | ≤±1 | %of IPN |
| εL | Linearity 0…IPN |  | ≤±0.5 | %of IPN |
|  | …3x IPN |  | ≤±1.0 | %of IPN |
| VOM | Residual voltage @ Ip=0,after an overload of 3 x IPN DC |  | <±0.7 | %of IPN |
| tra | Reaction time @ 10% of IPN |  | <3 | us |
| di/dtt | di/dt accurately followed |  | >50 | A/us |
| f | Frequency bandwidth(-3dB) |  | DC..50 | kHz |

| # General data |  |  |  |  |
| --- | --- | --- | --- | --- |
| TA | Ambient operating temperature |  | -10..+100 | C |
| m | Mass |  | 12 | g |

#### Remarks

- IS is positive when IP flows from terminals 1,2,3 4(IN)to terminals 8,7,6,5(OUT).

- This is a standard model .For different versions (supply voltages,turns ratios,unidirectional measurements….), please contact us.