CH-O-0200-0201                   * CH-O-0200-0201 is a Hall-Effect current transducer.

IPN =200A

Current Transducer                            * It can be used for the detection of DC, AC, pulse.

NO PHOTO

Advantages

- Easy mounting.

- Small size and space savings.

- Only one design for wide current ratings range.

- High immunity against external interference.

- Current overload capability.

- Adjustable output gain.

- Adjustable offset to zero

Applications

- AC motor speed control.

- Static converters for DC motor drives.

- Battery supplied applications.

- Uninterruptible Power Supplies (UPS).

- Power supplies for welding, cable TV and telecommunication applications.

Features

- Hall effect measuring principle.

- Galvanic isolation between primary and secondary circuit.

- Low power consumption.

| # Electrical data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| IPN | Primary nominal r.m.s current |  |  | 200 | A |
| IP | Primary current, measuring range |  |  |  600 | A |
| Vout | Analog output voltage @ IPN Ip=0 |  |  | 1.875 | V |
| RL | Output load resistance |  |  | ≥2 | k |
| Rout | Output impedance |  |  | <10 |  |
| VC | Supply voltage (± 5%) |  |  | 5 | V |
| IC | Idle current consumption @ VC =5V IP=0 |  |  | 22 | mA |

| # Accuracy – Dynamic performance data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| X | Accuracy @ IPN , TA = 25℃ | 5V (± 5%) | ≤±1 |  | %of IPN |
| εL | Linearity 0…IPN |  | ≤±0.5 |  | %of IPN |
|  | …3x IPN |  | ≤±1.0 |  | %of IPN |
| VOE | Electrical offset voltage @ IP = 0, TA = 25C @100 Amax 0 0 |  | < 20 | mV |  |
| VOM | Residual voltage @ Ip=0,after an overload of 3 x IPN DC |  | <±0.7 |  | %of IPN |
| tra | Reaction time @ 10% of IPN |  | <3 |  | us |
| di/dtt | di/dt accurately followed |  | >50 |  | A/us |
| f | Frequency bandwidth(-3dB) |  | DC..50 |  | kHz |

| # General data |  |  |  |  |
| --- | --- | --- | --- | --- |
| TA | Ambient operating temperature |  | -10..+110 | C |
| m | Mass |  | 20 | g |