Current Transducer CH-O-0200-0601                   IPN = 200A

* CH-O-0200-0601 is a Hall-Effect current transducer.

* It can be used for the detection of DC, AC, pulse.

| ### Electrical data |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| IPN | Primary nominal r.m.s current | ±200 |  |  |  | A |  |  |  |
| IP | Primary current, measuring range |  | ±600 |  |  | A |  |  |  |
| Vout | Analog output voltage @ Ip Ip=0 |  | VREF±(0.625·IP / IPN) |  |  |  |  | V |  |
|  | Ip=0 |  |  | VREF±0.025 |  |  |  | V |  |
| VREF | Internal Reference① Output voltage |  |  | 2.5±0.025 |  |  |  | V |  |
|  | VREF Output impedance |  |  | Typ. 200 |  |  |  |  |  |
|  | VREF Load impedance |  |  | ≥200 |  |  |  |  |  |
| RL | Output load resistance |  |  | ≥2 |  | k |  |  |  |
| Rout | Output impedance |  | <10 |  |  |  |  |  |  |
| CL | Max.output capacitive load |  | <1 |  |  |  | uF |  |  |
| VC | Supply voltage (± 5%) |  | 5 |  |  |  | V |  |  |
| IC | Idle current consumption @ VC =5V IP=0 |  | 22 |  |  |  | mA |  |  |

| ### Accuracy – Dynamic performance data |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| X | Accuracy @ IPN , TA = 25℃ | 5V (± 5%) |  |  | ≤±1 | %of IPN |
| εL | Linearity 0…IPN |  |  |  | ≤±0.5 | %of IPN |
|  | …3x IPN |  |  |  ≤±1.0 |  | %of IPN |
| VOM | Residual voltage @ Ip=0,after an overload of 3 x IPN DC |  |  |  | <±0.7 | %of IPN |
| tra | Reaction time @ 10% of IPN |  |  |  | <3 | us |
| di/dtt | di/dt accurately followed |  |  |  | >50 | A/us |
| f | Frequency bandwidth(-3dB) |  |  |  | DC..50 | kHz |

| ### General data |  |  |  |  |
| --- | --- | --- | --- | --- |
| TA | Ambient operating temperature |  | -10..+110 | ℃ |
| M | Mass |  | 20 | g |

Notes: ① It is possible to overdrive VREF with an external reference voltage between 2-2.8V providing its

ability to sink or source approximately 2.5mA.

## Features

- Hall effect measuring principle.

- Galvanic isolation between primary and secondary circuit.

- Low power consumption.

- Unipolar voltage supply.

- Multirange current transducer through PCB pattern lay-out.

## Advantages

- Small size and space saving

- Only one design for wide current ratings range

- High immunity to external interference.

- Internal & external reference

## Applications

- AC variable speed drives and servo motor drives

- Static converters for DC motor drives

- Battery supplied applications

- Uninterruptible Power Supplies (UPS)

- Switched Mode Power Supplies(SMPS)

- Power supplies for welding applications.

#### Remarks

- IS is positive when IP flows in the direction of the arrow.

- This is a standard model .For different versions (supply voltages ,unidirectional measurements….), please contact us.