CH-O-2000-1201                   * CH-O-(0500~3000)-1201 is a Hall-Effect current transducer.

IPN =2000 A

VOUT = 0…10V

Current Transducer                            * It can be used for the detection of DC, AC, pulse.

Advantages

- Easy mounting.

- Small size and space savings.

- Only one design for wide current ratings range.

- High immunity against external interference.

- Current overload capability.

- Adjustable output gain.

- Adjustable offset to zero.

Features

- Hall effect measuring principle.

- Galvanic isolation between primary and secondary circuit.

- Low power consumption.

Applications

- AC motor speed control.

- Static converters for DC motor drives.

- Battery supplied applications.

- Uninterruptible Power Supplies (UPS).

- Power supplies for welding, cable TV and telecommunication applications.

| # Electrical data |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| IPN | Primary nominal r.m.s current |  |  |  | 2000 | A |
| IP | Primary current, measuring range |  |  |  |  5000 | A |
| VSN | Rated voltage |  |  |  | ±4 | V |
| VC | Supply voltage ( 5%) |  |  |  |  15 | V |
| IC | Idle current consumption |  |  |  | < 30 | mA |
| Vd | AC isolation test, 50 Hz, 1min RM max |  |  |  | 2.5 | kV |
| RIS | Isolation resistance @ 500 VDC 0 22 |  |  |  | > 500 | M |
| VOUT | Output voltage @  IPN, RL = 10 k, TA = 25C |  |  |  | 0… 10 | V |
| RL | Load resistance |  |  |  | ≥ 10 | k |

| # Accuracy – Dynamic performance data |  |  |  |
| --- | --- | --- | --- |
| X | Accuracy @ IPN , TA = 25C (without offset) | <  1 | % |
| L | Linearity (0..  IPN) |   1 | %of IPN |
| VOE | Electrical offset voltage @ IP = 0, TA = 25C @100 Amax 0 0 | <  20 | mV |
| VOH | Hysteresis offset voltage @ IP = 0; |  |  |
|  | after an excursion of 3  IPN | <  30 | mV |
| VOT | Thermal drift of VOE | <  1 | mV/℃ |
| tr | Response time @ 90% of IP | < 10 | s |
| di/dt | di/dt accurately followed | > 50 | A/s |
| f | Frequency bandwidth (-3 dB) | DC…25 | kHz |

| # General data |  |  |  |  |
| --- | --- | --- | --- | --- |
| TA | Ambient operating temperature |  | -10..+100 | C |
| m | Mass |  | 280 | g |

SECONDARY TERMINALS

TERMINAL +: SUPPLY VOLTAGE + 15V

TERMINAL : SUPPLY VOLTAGE  15V

TERMINAL  OUT : OUTPUT MEASURE

TERMINAL  0: 0 V

Adjustment

OFS:Zero offset adjust

GIN:Output amplitude adjust

Direction of use:

Precaution -	Nominal current measuring range: 500A ~ 3000 A (AC) or 500 A ~ 3000 A (DC).

Output voltage: 0 ~ 10 V.

Or output current:  0～20mA.

If the above-stated condition is fulfilled, go to following steps:

Put the conducting wire through the center hole of the current transducer.

Connected the transducer as the pictures shown.

Adjust the OFS to obtain a zero offset output voltage if offset is non-zero. (EX-Factory is zero offset)

Adjust the GIN to obtain a desire maximum output voltage. (EX-Factory is 4V typical)